## Slide 1: Resource Adequacy and Planning Reserve Margins
Technical Conference on Capacity Planning and Resource Adequacy
Montana Public Service Commission
Helena, Montana
June 8, 2017
  Arne Olson, Partner

## Slide 2: Energy and Environmental Economics, Inc. (E3)
Fast-growing consultancy based in San Francisco
Rigorous analysis on a wide range of energy issues for utilities, regulators, government agencies, power producers, technology companies, and investors throughout North America and around the world
  Resource planning & procurement, asset valuation, cost of service & rate design, DER cost-effectiveness, energy storage analysis, renewable integration, transmission planning, deep decarbonization pathways
Our experience has placed us at the nexus of planning, policy and markets
Notes: 2

## Slide 3: INTRODUCTION: WHAT IS CAPACITY AND WHO IS RESPONSIBLE FOR IT?

## Slide 4: What is “capacity” and why is it important?
Capacity is the ability to generate electric energy at any given point in time
Utilities need adequate generation capacity to meet continuously-varying electric loads reliably over a broad range of conditions
The consequence of inadequate capacity is loss of load
  Loss of load is inconvenient, expensive, and potentially life-threatening
Utilities plan their systems to ensure that loss of load occurs very rarely
Source: http://www.energy.siemens.com

## Slide 5: Planning vs. operating reliability
Operating reliability
  Purpose: avoid cascading outages
  Utility function: Balancing Area operations
  Governed by: NERC and WECC
  Standards: NERC Control Performance Standards (CPS) and Balancing Authority Ace Limit (BAAL)
  Products needed: Operating reserves (regulation, freq. response, spin, & non-spin)
Planning Reliability
  Purpose: ensure sufficient capacity to meet load
  Utility function: resource planning and procurement
  Governed by: state and local authorities
  Standards: Planning Reserve Margin or Loss-of-Load standard (e.g., 1 day in 10 years)
  Products needed: generation capacity, dispatchable loads
Today’s topic

## Slide 6: “Pure capacity” vs. “Flexible capacity”
“Pure capacity” is the capacity needed to meet loads under all possible conditions, subject to acceptable reliability standards
  Pure capacity can be standardized and denominated in Effective MW
    Effective MW is often lower than Nameplate MW
  All Effective MW are the same
    An analytical process is needed to determine an Effective MW rating for each resource
“Flexible capacity” does not have a standard definition and is not a Resource Adequacy issue
  There are many attributes that contribute to power system flexibility: ramp rate, start time, min up/down time
  All resources are flexible to varying degrees
Today’s topic

## Slide 7: Who is responsible for ensuring adequate capacity?
FERC?
  Resource planning and procurement is state-jurisdictional
  Some states have opted to participate in organized wholesale electricity markets with FERC-jurisdictional capacity markets
NERC? WECC?
  NERC and WECC develop operating standards aimed at ensuring operational reliability
  NERC publishes information on resource adequacy planning but does not have mandatory planning standards
Utilities, state commissions and local governing bodies
  Utilities and their regulators are ultimately responsible for ensuring resource adequacy in their jurisdictions

## Slide 8: Why is resource adequacy important now?
Resumption of load growth and retirements of large power stations are creating the need to invest in new capacity
  Wave of construction after 2000-2001 energy crisis, combined with 2008 recession, created significant regional capacity surpluses
    Utilities frequently identified “Market Purchases” as a resource in IRPs
  Northwest Power and Conservation Council now estimates regional capacity shortfall in 2021
  Utilities are now identifying new capacity in IRPs
    Northwestern Energy: 400 MW of new gas-fired capacity
    Portland General Electric: 775-950 MW of new capacity
    Arizona Public Service: 5400 MW of new gas-fired capacity

## Slide 9: Why don’t wholesale markets build capacity on their own?
Wholesale markets facilitate more efficient operations and exchange of surplus energy
Western Interconnection is still dominated by vertically-integrated utility systems, in which new capacity is backstopped by captive ratepayers
  Developed by utilities as rate-based asset or procured from third parties via long-term PPA
Even “organized markets” in regions with retail competition have required “bolt-on” capacity auctions to incent new construction
  ERCOT is lone exception

## Slide 10: Methods and PRACTICES for determining prm

## Slide 11: How do utilities ensure that they have adequate capacity?
Utilities calculate a Planning Reserve Margin (PRM) to account for operating reserves, extreme weather, generation outages
  PRM = % above 1-in-2 (average year) peak load
  Typical range is 12-20%
  PRM used as an entry in load-resource table for determining resource need
Unit | MW
Natural Gas | 1,809
Colstrip | 296
Hydro Projects | 575
Mid-C Hydro Agreements | 123
Other Contracts | 9
DSM | 126
Renewables | 127
Imports | 92
Total Available Dependable Capacity | 3,157
1-in-2 Peak Load | 3,525
Planning Reserve Margin | 550
Total Dependable Capacity Needed | 4,075
Dependable Capacity Shortage | 918
PRM (%) | 15.6%
Example Load-Resource Table
Source: Portland General Electric, August 2015

## Slide 12: How do utilities determine the right Planning Reserve Margin?
PRM is a simple concept, however calculations can be quite detailed
Practices for calculating a PRM are widely varied across the industry. Some examples include:
  PRM of 15% based on its common use across the industry
  Rule of thumb: 6% for operating reserves + 3% for forced outages + 3% for more extreme weather
  PRM based on largest single generator or transmission outage
  PRM based on detailed loss-of-load probability (LOLP) study

## Slide 13: Industry “best practice”: reliability study based on LOLP
Evaluate possible load and resource conditions over thousands of simulated years to determine resources needed to meet defined reliability target
  Reliability target is typically defined as “1 day in 10 years”, though again there is no industry standard
  Reliability is modeled using Loss-of-Load Probability (LOLP) modeling techniques
Definition of reliability metrics:
  Loss of Load Probability (LOLP): Prob. shortfall in a given hour
  Loss of Load Expectation (LOLE): Expected hours of capacity shortfall over a year, sum of LOLP across the entire year
  Expected Unserved Energy (EUE): Expected load not served over a year, sum of LOLP x MW shortfall across the entire year
  Effective Load-Carrying Capability (ELCC): Quantity of additional load that can be served by variable resources while maintaining reliability

## Slide 14: Conventional generators are not 100% reliable
LOLP analysis calculates a distribution of conventional generation availability based on forced outage rates
  Generator 1 = On (P=95%) or Off (P=5%)
  Generator 2 = On (P=97%) or Off (P=3%)
  Etc.
Probability
Available Thermal Generation (MW)
Distribution represents probability that the portfolio has a given quantity of available capacity
Distribution is wider, and required PRM is higher, if:
  System has few generators
  Resources have higher outage rates

## Slide 15: Loss of load occurs when available generation is less than load
Loads also vary significantly due to weather
Load distribution
Generation distribution
Load
Generation
LOLP
Load > Generation
Load is most likely to exceed generation during hours with high load, high generator outages, or both

## Slide 16: “Heatmap” shows when loss of load occurs on a given system
Chart shows hours of LOLP by month/hour timeslice
Sum of time slices is test year LOLE
Month
HE PST
Source: Portland General Electric, August 2015

## Slide 17: Planning criteria used by utilities are widely varied
 | Peak Demand in 2021 (MW) | Planning Criterion | PRM | Peak Season
Puget Sound Energy | 7,000 MW | LOLP: 5%* | 16% (2023 - 2024) | Winter
Avista | Summer: 1,700 MW; Winter: 1,900 MW | LOLP: 5%* | 22% (14% + operating reserves) | Both
PacifiCorp | 10,876 MW | LOLE: 2.4 hrs/ year | 13% | Summer
Arizona Public Service | 9,071 MW | One Event in 10 Years | 15% | Summer
Tuscon Electric Power | 2,696 MW | PRM | 15% | Summer
Public Service Co. of New Mexico | 2,100 MW | LOLE: 2.4 hrs/ year | Greater of 13% or 250 MW | Summer
El Paso Electric | 2,000 MW | PRM | 15% | Summer
Cleco | 3,000 MW | LOLE = 1-day-in-10 yrs. | 14.8% | Summer
Kansas City Power & Light | 483 MW | Share of SPP** | 12%** | Summer
Oklahoma Gas & Electric | 5,500 MW | Share of SPP** | 12%** | Summer
South Carolina Electric & Gas | 5,400 MW | 24 to 2.4 days/10 yrs | 14-20% | Both
Tampa Electric | 4,200 MW | PRM | 20% | Both
Interstate Power & Light | 3,300 MW | PRM | 7.3% | Summer
Florida Power and Light | 24,000 MW | PRM | 20% | Both
California ISO | 52,000 MW | LOLE: 0.6 hours/year | 15-17% | Summer
* PSE and Avista use NWPCC criterion of 5% probability of shortfall occurring any time in a given year
** SPP uses 1-day-in-10 years or 12% PRM system-wide

## Slide 18: RENEWABLES AND FLEXIBLE CAPACITY

## Slide 19: Renewable resources contribute to resource adequacy
No resource is perfectly available to help reduce LOLP
By convention, dispatchable resources rated at nameplate and forced outages factored into PRM
Non-dispatchable resources assigned “effective capacity” rating
Chart: 
| Fossil Generation | Wind Generation | Solar Generation
 | 95 | 20 | 60
 | 5 | 80 | 40

60 MW Capacity Value
100 MW nameplate
20 MW Capacity Value
95 MW Capacity Value
Illustrative Capacity Values

## Slide 20: Methods for estimating capacity credit of renewables
Heuristic approximations
  Time window methods
    Average or percentile capacity factor during highest load hours
    Currently the most common industry method due to ease of calculation
  Simple and easy to understand but increasingly inaccurate at high penetrations
Reliability based methods
  Effective Load Carrying Capability (ELCC)
    After new variable generation is added to a system, ELCC is defined as the additional load that can be added to the system while still maintaining the original system reliability (original annual LOLE)
  Accurate but computationally intensive
Accurately measuring the contribution of renewable energy becomes increasingly important as its share of system capacity grows!

## Slide 21: Methods for estimating capacity credit of renewables vary widely
 | Approach | Notes
BPA | Time window | Wind is assigned zero value
California PUC | Time-window | Dec-Mar, 4-9 pm, Apr-Oct, 1-6 pm
Idaho Power | Time-window | Summer, 3-7 pm
ISO New England | Time-window | Jun-Sep, 2-6 pm
New York ISO | Time-window | Jun-Aug, 2-6 pm, Dec-Feb, 4-8 pm
Ontario IESO | Time-window | Capacity factor over the top 5 contiguous daily peak demand hours
PJM | Time-window | Jun-Aug, 4-6 pm
PNM | Time-window | Peak hour
Quebec Balancing Authority Area | Other | Monte Carlo analysis supplemented by analysis of fourteen critical extreme cold weather events
Arizona Public Service | ELCC | Average capacity value over several years of LOLE simulations
BC Hydro | ELCC | 
ERCOT | ELCC | 
Midwest ISO | ELCC | 
PSCO/Xcel | ELCC | Based on 10-year ELCC study

## Slide 22: Effective Load-Carrying Capability
Adding renewables reduces LOLE due to expectation of non-zero production
Adding load returns system to the original LOLE
The amount of load that can be added to the system is the Effective Load-Carrying Capability (ELCC) of the renewables
Original system LOLE
LOLE after renewables
Additional load to return to original system LOLE
= ELCC

## Slide 23: ELCC method: Subtract renewables from load in LOLP calculations
Renewable production is subtracted from gross load to yield “net load”, which is always lower
LOLP decreases in every hour
Gross load distribution
Net thermal generation distribution
Net load distribution with renewables
Renewable
net load
Gross load
Thermal generation
Reduction in LOLP with increase in renewables

## Slide 24: Factors that affect the capacity value of variable generation
Coincidence with load
  Resources with better correlation with high load periods have higher ELCC
Coincidence with existing portfolio
  Adding more capacity of the same type results in lower marginal value
  Adding diversity results in higher marginal value
Variability
  Statistically, the possibility of low production during a peak load event reduces the value of a resource
August
Weekday, HE17

## Slide 25: How is “Flexible Capacity” related to Resource Adequacy?
Limited Ramping Capability
Unserved Energy
Limited Ramping Capability
Renewable Curtailment
Strategy to Minimize Downward Violations
Strategy to Minimize Upward Violations
Without renewable dispatch: shedding of firm load required
With renewable dispatch: no load shedding required
Capacity does not need to be “flexible” for Resource Adequacy purposes, but flexibility does help with operations & curtailment. Key question: how much to pay for additional flexibility?
Under flexibility-constrained operations, reliability can be maintained through renewable dispatch, at the cost of lost production

## Slide 26: Role of regional market

## Slide 27: Interactions with the regional market
Conventional methods effectively assume that each system is an island
  Long-term contracted resources treated as owned
  Generic imports can be represented as a resource, perhaps with transmission outage rate
Many utilities rely on “market purchases” to fill energy and capacity gaps
  Based on assumed availability of resources
  Regional market conditions typically not analyzed rigorously
  How much capacity can a utility count on being able to acquire from its neighbors?

## Slide 28: Are current practices sufficient to maintain reliability?
Current practices rely on 16 states & provinces and many local jurisdictions to adopt practices that maintain reliability across our multi-state regional grid
Current system can work as long as:
  Every utility calculates its own needs in a sufficiently robust manner
  Every utility builds or identifies physical resources to meet its own needs
  New resource additions are approved in a timely manner
However, analysis is complex and often contentious

## Slide 29: Benefits of regional planning reserve sharing
Regional planning reserve sharing would take advantage of load and resource diversity that exists across regions
  A system in which each utility builds physical assets to meet its own needs will result in overcapacity, because not every system peaks at the same time
    Planning to meet regional coincident peak loads requires less capacity than meeting each individual utility’s peak loads
    Resources that are surplus in one area could be utilized to meet a deficit in a neighboring area
  Larger systems require lower reserve margins because they are less vulnerable to individual, large contingencies
  Regional entity could adopt more sophisticated practices and computer models than individual utilities
  Regional entity would provide calculation of capacity need that is independent from the utility

## Slide 30: conclusion

## Slide 31: Key questions for regulators in assessing resource adequacy
How accurate or reliable is the utility’s peak load forecast?
How robust is the utility’s method for determining its Planning Reserve Margin?
How accurate is the utility’s method for estimating the capacity contribution of renewables?
How can the utility know how much capacity is available in the regional market?
How much should utility be willing to pay for flexible capacity?

## Slide 32: Thank You!
Energy and Environmental Economics, Inc. (E3) 101 Montgomery Street, Suite 1600 San Francisco, CA 94104 Tel 415-391-5100 Web http://www.ethree.com
Arne Olson, Partner (arne@ethree.com)